[image: image1.wmf] 

30

A

 

[image: image2.wmf] 

N

 


                LG Dynamic Braking Units

SV-DBU-U Series[image: image3.wmf] 

N

 


[image: image4.wmf] 

N

 

[image: image5.wmf] 

N

 


[image: image6.emf]


[image: image7.wmf]nit

B

raking

U

B2

B1

B1

N

G

P

B2

D

ynamic

RUN

OHT

FOT

OCT

N

V

W 

U

R

T

S

(P2)

P

POWER

IM

WIRING




 LGIS constantly endeavors to improve its products so that information in this manual 

 is subject to change without notice.                                      

                                                                    Ver. 1.0  2001. 9
Overview


SV-DBU-U series is designed to use with LG inverter SV-iS5 and SV-iH series. 

This manual describes the safety instructions that must be followed when installing, operating, and servicing. Read this manual completely before installing. The unit contains high voltage that can cause electric shock resulting in personal injury or loss of life.


Important User Information

                                Indicates that incorrect handling may cause 

                                hazardous conditions, resulting in personal injury or 

                                loss of life.

                                Indicates that incorrect handling may cause 

                                physical damages.

     "CAUTION" level instructions may lead to a serious result according to conditions.       

      Please follow the instructions of caution level for safety.

· Safety Instructions

1. Electric Shock


· Do not open the front cover when the input power is introduced. 

· Be sure to remove all input power from the braking unit including drive 

    before servicing.

· Wait at least 10 minutes before servicing and check the residual voltage.

· Service only qualified personnel.

2. Fire


· Mount the braking unit and resistor on a non-flammable material. 

    Installing them on a flammable material may cause a fire.

· Do not connect the braking resistor directly to the DC terminal (P2, N) of

    the drive. This can cause a fire.

3. Injury


· Do not apply voltage to the terminals higher than the voltage specified in 

    the manual. This can cause damage and burst of the unit.

· Be sure to connect wires to the correct terminal. Especially, ensure the 

    polarity of DC power terminal. Otherwise, damage and burst of the unit 

    may occur.

· Do not touch the resistor right after the power is turned off. The resistor is still

    hot.

4. Other Instructions


· Do not operate the unit if enclosure damaged.

· Prevent any wire fragments, metallic particles from dropping during 

    installation.

1. 
Nomenclature


	LG 

Drives
	Symbol
	Drive Capacity
	
	Symbol
	Type
	
	Symbol
	Drive Input Voltage

	
	150
	11~15[kW]
	
	DBU
	Dynamic Braking Unit
	
	2U
	200V Class

	
	220
	18.5~22[kW]
	
	
	
	
	4U
	400V Class

	
	370
	30~37[kW]
	
	
	
	
	
	

	
	550
	45~55[kW]
	
	
	
	
	
	

	
	750
	75[kW]
	
	
	
	
	
	


2. Specifications

2.1 200V Class

	
	SV150DBU

-2U
	SV220DBU

-2U
	SV370DBU

-2U
	SV550DBU

-2U

	Max. DC Input Voltage
	DC 400V

	Applicable Drive 

Capacity [kW]
	11
	15
	18.5
	22
	30
	37
	45
	55

	Braking Resistor
	Wattage
	3.2 [KW]
	4.8 [KW]
	6.4 [KW]
	9.6 [KW]

	
	Minimum Resistance
	8.5 [Ω]
	5.7 [Ω]
	4.2 [Ω]
	2.8 [Ω]


2.2 400V Class

	
	SV150DBU-4U
	SV220DBU-4U
	SV370DBU-4U
	SV550DBU-4U
	SV750DBU-4U

	Max. DC Input Voltage
	DC 800V

	Applicable Drive 

Capacity
	11
	15
	18.5
	22
	30
	37
	45
	55
	75

	Braking Resistor
	Wattage
	3.2 [KW]
	4.8 [KW]
	6.4 [KW]
	9.6 [KW]
	12.8 [kW]

	
	Minimum Resistance
	8.5 [Ω]
	5.7 [Ω]
	4.2 [Ω]
	2.8 [Ω]
	8.4 [Ω]


2.3 General Specifications

	Average Braking Torque
	100%

	Enable Duty
	10% (without cooling fan on heat sink)

	Parallel Connection
	Connectable up to 3 units in parallel

	Maximum Turn On Time
	6 seconds

	Output Signal
	Heat Sink Overheat, Fuse Open, OC Trip

	Protection
	Heat Sink Overheat Protection, Over-Current Protection, Output Short Circuit Protection

	Environmental Conditions
	Operating Temperature
	-10℃ ~ 40℃

	
	Humidity
	Less Than 90 % RH Max. (Non-Condensing)

	
	Altitude
	1,000m above sea level

	
	Cooling Method
	Natural Convection

	
	Application Site
	No Corrosive Gas, Combustible Gas, Oil Mist, or Dust


3. Installation

· Environmental Conditions

1) Do not mount the unit in direct sunlight. Isolate the unit from excessive vibration.   

2) Protect the unit from moisture, dust, metallic particles, corrosive gases and liquids. Install the units on a non-flammable material and as smooth as possible.

3) In case of installing many units in a panel, consider the air flows for power dissipation. (see below figures for proper installation)


                        GOOD                       BAD
<<Installing units in a panel>>


                        GOOD                            BAD
<<Fan location in a panel>>

· Mounting

The units must be mounted vertically with sufficient room (horizontally and vertically) from adjacent equipment.


4. Terminal Configuration

1) Power Terminals


	Terminal
	Description

	P
	DC (+) input. Connect to “P2” or “P” terminal of drive

	N
	DC (-) input. Connect to “N” terminal of drive 

	G
	Ground Terminal

	B1
	Connect to braking resistor

	B2
	Connect to braking resistor


2) Control Terminals


	Terminal
	Function     

	IN+
	Slave turn on signal input (when “Slave Mode” selected)

	IN-
	Slave turn on signal input (when “Slave Mode” selected)

	OUT+
	Slave turn on signal output (when “Master Mode” selected)

	OUT-
	Slave turn on signal output (when “Master Mode” selected)

	30A
	Fault signal output

30A : Normal open contact  

30B : Normal close contact     

30C : Common terminal

	30B
	

	30C
	


        (Refer to sec. 7 for details of Master/Slave Operation)

5. Terminal Wiring

· The SV-iH series has two kinds of power terminal configurations. Make sure the wiring according to drive capacity.
· SV030iH-4, SV037iH-4, SV045iH-4, SV055iH-4 units do not provide terminals for DC reactor connection.
1) Wiring Drive, DB unit and DB resistor 












2) Wiring Drive, DB unit, DB resistor and DC reactor
      
6. Basic Wiring
1) Single Operation










* )  The SV030/037/045/055DBH-4 units provide only terminal “P” instead of terminal “P1” and “P2”. Please refer to “2) Wiring Drive, DB unit and DB resistor for SV030/037/045/055iH-4” for correct wiring.
· Use twist wire shorter than 10m between drive, DB unit and DB resistor.

· In case of master/slave operation, the control wire should be shorter than 2m with twist wire.

· Be sure to earth terminal “G” of drive and DB unit.

· Wire Size:

	DB Unit
	Wire size

	200V
	SV150DBU-2U
	5.5㎟  

	
	SV220DBU-2U
	8.0㎟  

	
	SV370DBU-2U
	14.0㎟  

	
	SV550DBU-2U
	14.0㎟  

	400V
	SV150DBU-4U
	5.5㎟ 

	
	SV220DBU-4U
	5.5㎟  

	
	SV370DBU-4U
	5.5㎟  

	
	SV550DBU-4U
	8.0㎟  

	
	SV750DBU-4U
	14.0㎟  


7. 7. Master / Slave Operation

1) In case of parallel operation of two braking units, the one must be set at “Master” and the other at “Slave”. (When one braking unit is operated it must be set at “Master” : Factory default – “Master”)

2) How to set to Master (on PCB)

·  Set the “Select Switch JP1” as below figure.


3) How to set to Slave (on PCB)

·  Set the “Select Switch JP1” as below figure.


4) Connection between Master and Slave

·  Set one DB unit to “Master” and the other to “Slave”.

·  Connect “OUT+” terminal of Master to “IN+” terminal of Slave and “OUT-” 

terminal of Master to “IN-” terminal of Slave.


5) Connecting 3 DB Units

· Set one DB unit to “Master” and others to “Slave”.
· Connect “OUT+” terminal of Master to “IN+” terminal of Slave and “OUT-” 
terminal of Master to “IN-” terminal of Slave, respectively.










6) Master/Slave Operation



















8. Combination of DB Units according to Drive Capacity
1) Combination of Braking Units 
· 200V Class

	Applicable Drive [KW]
	11
	15
	18.5
	22
	30
	37
	45
	55

	Braking Unit
	SV150DBU-2U
	SV220DBU-2U
	SV370DBU-2U
	SV550DBU-2U

	Braking Resistor
	3.2KW 8.5Ω
	4.8KW 5.7Ω
	6.4KW 4.2Ω
	9.6KW 2.8Ω

	Applicable Motor [KW]
	11
	15
	18.5
	22
	30
	37
	45
	55


· 400V Class

	Applicable Drive [KW]
	11
	15
	18.5
	22
	30
	37

	Braking Unit
	SV150DBU-4U
	SV220DBU-4U
	SV370DBU-4U

	Braking Resistor
	3.2KW 33.9Ω
	4.8KW 22.8Ω
	6.4KW 16.9Ω

	Applicable Motor [KW]
	11
	15
	18.5
	22
	30
	37


	Applicable Drive [KW]
	45
	55
	75
	90 ~ 160
	220

	Braking Unit
	SV550DBU-4U
	SV750DBU-4U
	SV750DBU-4U 

* 2 EA
	SV750DBU-4U 

* 3 EA

	Braking Resistor
	9.6KW 11.4Ω
	12.8KW 8.4Ω
	12.8KW 8.4Ω 

* 2 EA
	12.8KW 8.4Ω 

* 3 EA

	Applicable Motor [KW]
	45
	55
	75
	90 ~ 160 
	220 


· See below for the combination of DB Units and DB resistors.
2) Combination of 200V Class Units

  ▶ Drive Capacity: 30[kW] ~ 37[kW]       ▶ Drive Capacity: 45[kW] ~ 55[kW] 


3) Combination of 400V Class Units

▶ Drive Capacity: 30[kW] ~ 37[kW]       ▶ Drive Capacity: 45[kW] ~ 75[kW]

  ▶ Drive Capacity: 90[kW] ~ 160[kW]


  ▶ Drive Capacity: 220[kW]


9. Display LED and Fault Reset

The DB Unit have four LEDs on the frontcover. The green LEDs display main power input and braking operation. The red LEDs display fault status of the unit.

	Display
	Function

	POWER

(RED)
	This LED is turned on when the input power of the unit is introduced.

	RUN

(GREEN)
	This LED is turned on when the unit is in the braking operation.

	OHT

(RED)
	This LED is turned on and cut off (trip) the output when the heat sink of the unit is over heated.

	OCT

(RED)
	This LED is turned on when an excessive current flows through the IGBT and the unit cut off the output to protect the unit.

	FOT

(RED)
	This LED is turned on when the internal protective fuse is opened.


10. Dimensions

                                                              Units: [mm]





OUT+





IN-





G





P





N





EB Resistor





DB Resistor





DB Unit





Spec.





TH2





TH1





30A





5M max.





B1





B2





B2





B1





�





30B





30C





G

















30C





2m max.





SLAVE PCB





MASTER PCB





N





30B





16.9Ω, 6.4kW





16.9Ω, 6.4kW





DB


Resistor





DB


Resistor





DB Unit





SV075DBU-4U





16.9Ω, 6.4kW





16.9Ω, 6.4kW





16.9Ω, 6.4kW





16.9Ω, 6.4kW





DB


Resistor





DB


Resistor





DB


Resistor





DB


Resistor





SV075DBU-4U





SV075DBU-4U





DB Unit





DB Unit





Drive





16.9Ω, 6.4kW





16.9Ω, 6.4kW





16.9Ω, 6.4kW





16.9Ω, 6.4kW





DB


Resistor





DB


Resistor





DB


Resistor





DB


Resistor





DB Unit





DB Unit





Drive





SV075DBU-4U





SV075DBU-4U





P





USER’S MANUAL





P1





P2





J13





IN+





IN-





5M max.





N





P





LG Industrial Systems





DB Unit





DB


Resistor





MASTER DB Unit





16.9Ω, 6.4kW





DB


Resistor





16.9Ω, 6.4kW





SV075DBU-4U





Drive





1m max.





SLAVE PCB1





MASTER PCB





J13





Air flow





IN+





IN-











Drive





OUT+





OUT-





DB Unit or


DB Resistor 





IN+





IN-











OUT+





OUT-





IN+





J13





B1





OUT+





OUT-





B2





IN+





IN-





J13





SLAVE PCB2





Twist pair





IN-





OUT+





OUT-





OUT+





OUT-





J13





SLAVE





MASTER





SLAVE








PRELIMINARY





MASTER





Twist pair





IN+





TH2





TH1





5M max.





B1





B2





B2





B1





2M max.





OUT-





5M max.





G





P





N





Spec.





Input


Power





P1





G





�





P2





Motor





IM





W





U





V





T





S





R





Drive








전원











P1

















G








DB Resistor





SLAVE DB Unit





�





P2





Motor





IM





TH2





TH1





W





U





V





T





S





R





1m max.





Drive





MCCB





B1





N





B2





B1





DC Reactor





B2





B1





G





N





P





P1





P2





�





DB Resistor





DB Unit





DB Resistor





B2





B1





DB Unit





B2





B1





G





DB Unit





DB


Resistor





16.9Ω, 6.4kW





SV037DBU-4U





DB Unit





OUT-





OUT+





IN-





IN+





B2





B1





G





DB Unit





DB


Resistor





Drive





Drive





P











Type





MCCB





over 50mm





over100mm





over 100mm





over 50mm





4.2Ω, 6.4kW





DB


Resistor





Common bus bar





�





SV-DBU





DB Unit or


DB Resistor 





DB Unit or


DB Resistor 





DB Unit or


DB Resistor 





Cooling fan





DB Unit or


DB Resistor 





4U





DBU





150





-





SV





Type





  !  CAUTION 





  !  CAUTION 





  !  CAUTION 





  !  WARNING





  !  CAUTION 





  !  WARNING















































4.2Ω, 6.4kW





SV037DBU-2U





SV037DBU-2U





Drive





Drive








B2








DB Unit or


DB Resistor 





DB Unit or


DB Resistor 





DB Unit





DB


Resistor











4.2Ω, 6.4kW








SV037DBU-2U








